01 FEB 07

Basis of Design Document for LEED Fundamental Commissioning
Project:



Approved:








Name

Design Agent’s Representative

Date


Name

Commissioning Authority

Date

Overview and Instructions
The purpose of this document is to provide clear and concise documentation of the Designer’s response to the Owner’s goals, expectations and requirements for commissioned systems, and shall be utilized in conjunction with the Owner’s Project Requirements Document for LEED Fundamental Commissioning throughout the project delivery and commissioning process to provide an informed baseline and focus for design development and for validating constructed systems’ energy and environmental performance. 

The Basis of Design Document for LEED Fundamental Commissioning is a required document for LEED Version 2.2 EA Prerequisite 1, Fundamental Commissioning of the Building Energy Systems. It shall be completed by the Designer and shall be reviewed and approved by the Design Agent (as Owner’s representative) and the Commissioning Authority.
Use of this template is not required, nor are there any restrictions on editing of it. It is provided simply as a tool to assist project teams in meeting the documentation requirements for LEED Fundamental Commissioning.

This template has not been coordinated with the requirements of ASHRAE Guideline 1, The HVAC Commissioning Process. If compliance with ASHRAE Guideline 1 is required, this document must be edited as needed to comply. 

The Basis of Design Document for LEED Fundamental Commissioning shall be submitted with each design submittal, updated as design progresses, and submitted complete as part of the final design submittal. It must be completed prior to the approval of Contractor submittals of any commissioned equipment or systems to meet LEED requirements. Subsequent updates to the document will be made as needed during the as-built phase. Development of and all updates to this document shall be made by the Designer and approved by the Design Agent (as Owners Representative) and the Commissioning Authority.

The intent of the Basis of Design Document for LEED Fundamental Commissioning, per the LEED v2.2 Reference Guide, is to describe the design of systems to be commissioned and outline any design assumptions that are not otherwise included in the design documents. This template contains the basic recommended components indicated in the LEED v2.2 Reference Guide. It shall be adapted as needed to suit the project, remaining reflective of the LEED intent.

The document shall address the primary areas related to energy use and comfort for which the design intent and basis of design should be defined.  The design intent provides the explanation of the ideas, concepts and criteria that are considered to be very important to the owner, coming out of the programming and conceptual design phases.  The basis of design is the documentation of the primary thought processes and assumptions behind design decisions that were made to meet the design intent.  The format merges the salient parts of the design intent and basis of design. The design intent evolves from more general descriptors during the conceptual design, to more specific descriptors during actual design, to in-depth and specific descriptors during the specifying stage, which are finalized during the as-built phase. As part of the design narrative, one-line CAD drawings shall be developed for the systems listed in the Design-Phase Commissioning Plan.
Under each area or building system is an outline of pertinent questions and data needed.  Sequences of operation for all outlined dynamic systems and components should be clearly documented. Attaching equipment manufacturers’ sequences may acceptable, but will generally require additional narrative.

Updates to the Basis of Design Document for LEED Fundamental Commissioning throughout the course of project delivery shall be made by the Designer based on decisions and agreements coordinated with and agreed to by the Design Agent as Owner’s representative and the Commissioning Authority.

The Basis of Design Document for LEED Fundamental Commissioning shall be included in the project’s LEED documentation file under EA PR1, Fundamental Commissioning of the Building Energy Systems.  


Basis of Design Document for LEED Fundamental Commissioning

Contents
1. General Building Design, Function and Landscaping
· Overview

· Sustainable construction and environmental compatibility

· Indoor environmental quality—thermal, air distribution, acoustics, air quality, visual quality 

· Landscaping

2. HVAC Systems and Design Parameters
· Overview

· Design conditions and load assumptions

3. Chiller System (Chillers, Cooling Towers, Pumps, Piping)

4. Boiler and Heating Water System

5. Roof Top Packaged System(s)
6. VAV Terminal Units – Air Conditioning Only (TU-AC) 

7. VAV Terminal Units – Reheat (TU-RH) 

8. Heat Recovery Unit (HRU)
9. Computer Room Air Conditioning Unit (CRACU)
10. Daylighting Controls

11. Lighting Sweep Control

12. Building Automation System (BAS)
13. Split Air Conditioning; Heat Pump System
14. Emergency Power System

1
General Building Design, Function, and Landscaping

1.1 General Building Design and Function 


What are the general design objectives regarding energy efficiency?

Comfort and indoor environmental quality?

Sustainability and environmental compatibility?

Other:

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?
1.2  Sustainable Construction and Environmental Compatibility

Design Intent


What are the objectives regarding sustainability and environmental compatibility?

Basis of Design-General Description and Function

How will the building/grounds systems meet the design intent?

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

1.3  Indoor Environmental Quality

Design Intent

What are the general objectives for indoor environmental quality?

Thermal Comfort—General Description and Function

Record the occupant activity and design temperatures for the various spaces in Table 1.

Air Distribution

What issues were considered in choosing diffusers?

Is the return air (RA) ducted or open-plenum? Why?

Are the RA grills in every room?  Why?

What special considerations are being given to spaces with high solar load regarding cooling, large glazed areas, cold-air convective drafts, etc.? What solutions were used?

Acoustics


What is the design NC (noise criteria) sound level?  Provide this information in Table 1.  Are there any special acoustical considerations for any areas (areas close to the AHU, private areas, open office areas, etc.)?  How will this criteria be met? (flexible duct, duct lining, fan type, lead wraps, diffuser type, TU damper type, etc.)

Noise class (NC) 35-40 for closed offices and 41-43 for open offices, recommended by ASHRAE)

Air Quality


For the general building and individual spaces, what is the desired outside air fraction or cfm per person and the number of persons per square foot?  (Provide this information in Table 1).  Is the outside air (OSA) controlled by CO2 monitors?  Explain. Are there airflow measurement devices provided?
Can occupants adjust ventilation?  How and what limits apply to what areas?

Are there any special indoor pollutant source concentrations?  How are they handled?  List areas served by exhaust fans, the fan size, air changes per hour and operational control.

Is smoking of tobacco products allowed in or near the building? Y/N

How will the fresh air rate be maintained at low supply air volumes of the VAV system?  Are perimeter zones treated differently than interior zones (reheat box damper settings, etc.)?

Where are the outside air intakes located?  Are they near any potential sources of pollutants?

Are full-drain condensate pans used in the air handler units?   (Yes / (No

What other special IAQ issues were considered?

Visual Quality

What are the design footcandle levels for the various spaces? (Provide this information in Table 1). Why? Is additional task lighting assumed?

Do any spaces have special glare requirements?   (Yes / (No

How will they be met?  (special light fixtures and lenses, fixture layout, special CRT screens, etc.)

How will glare be controlled in daylit areas?

What are the parameters and sequences of operation for the daylighting controls and dimming lights? How will occupants interact with the system (overrides, education, etc.)?

Can occupants adjust the lighting system?

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

1.4  Landscaping


Design Intent

Describe the objectives and the elements of the specific landscape design that contribute to energy efficiency, water conservation, and comfort.
Sequences


What are the main control sequences for the watering systems that ensure water conservation?

Maintenance

Are there any special instructions as to the care of the landscape elements that will enhance or degrade their energy and comfort benefits?  (refer to O&M manual sections, if applicable)

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

1.5  Interior Conditions Basis of Design


Table 1
Reception, records, conference room, closed offices, open offices, exercise room, lunch room, inventory, stock, etc.

	
Space
	
Use /
Activity
	
Occupant Type
	
Num of Occs
	
Operating Hours per Day
	
Design Cooling DB
	Design Cooling WB or RH
	Design Heating DB
OSAT
	OSA CFM / Person or CO2
	Design Noise Level (NC)
	Design Light Level
(FC)

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	


2
HVAC Systems and Design Parameters

2.1  General

General description of the main HVAC systems and areas served.


System




Areas Served

Why were the above particular systems chosen?

Describe the level of priority given to energy conservations for the system.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

2.2  Specific System Descriptions 


	
System
	Heating / Cooling / Both
	
Areas Served

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


What is the rationale for the way the HVAC and lighting were zoned?

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

2.3  Load Calculations

What outdoor design conditions were assumed for load calculations?

Summer:  DB______  WB______    
Winter:  DB______

What indoor design conditions were assumed for load calculations?

Summer:  DB______  RH______
Winter:  DB______  RH______

Internal load assumptions:  Lighting: ______W/sf.  Misc: ______W/sf.  Other:


SF/Person: ______  Btu/hr/person: sensible ______, latent ______  

Ventilation: ______cfm/person.   Basis (code, etc.):


Infiltration: ( ______cf,/sf wall area, or ( ______ air changes per hour.

	Glazing:
	Orientation
	% of Wall Area
	Overall U
	SC

	
	N
	
	
	

	
	S
	
	
	

	
	E
	
	
	

	
	W
	
	
	


What overall safety factor was used and how much diversity was assumed for the heating, cooling plant and fan size?

For redundant equipment, what redundancy criteria were used?

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

(Complete the following sections for each commissioned system as applicable or indicate “N/A”. Add sections with similar information  for additional other anticipated commissioned systems as applicable)
3
Chiller System   (Chillers, Cooling Towers, Pumps, Piping)

3.1  Design Intent (Provide this information for each chiller)

What is this chiller system used for? ( Supplies chilled water to air handler units to cool building space.      ( Computer room AC units.             ( Process chilled water
( Heat recovery for: 


Other:


What areas of the building do this chiller serve?




List the areas that this chiller does not serve?




What types of air conditioning equipment serve the areas not served by this chiller?




What vibration and noise considerations are given to the location of this chiller? 







What energy efficiency objectives are there for the chiller system? ( Highly efficient, ( Moderately efficient, ( Standard efficiency

What level of automatic control features are desired for this chiller system relative to automatic staging, optimization, central building automation system monitoring and control capabilities, etc.? ( Highly automated, ( Moderately automated, ( Minimally automated

What type of refrigerant will be used and why?




3.2  Basis of Design-Components Description and Methods for Meeting Design Intent
Chillers

Briefly describe the chiller system.

	( Centrifugal    ( Screw

( Hermetically sealed

( Heat recovery

( Refrigerant type:_________

( Air cooled    ( Water cooled  
( Evaporative cooled

( Capacity control type: ( Prerotation vanes
( Other:__________________
	
	( Reciprocating chiller

( Heat recovery

( Refrigerant type: ______________

( Air cooled   ( Water cooled
( Evaporative cooled

( Stages of unloading:____________
( Other:_______________________


How many chillers of each size are there? (size and number of each size): 




Is there a standby / redundant chiller during design conditions?________

Are there isolation valves for when only one chiller is running? ________________________

What method was used for determining the design cooling load? 




Attach load calculations and assumptions, if not given in a previous section. (Diversity, safety factor, outdoor DB, WB, indoor DB, lighting W/sf, plug loads W/sf, sf/person, ventilation cfm/person, infiltration rate, glazing % of wall, overall U; SC).

Describe any provisions in the chiller system for accomodating future building or load expansion.







What evidence can be provided to show the chillers are not oversized? 






Why were they chosen to be different or equal size?_





Was variable compressor speed seriously considered?  If not, why not? 






Was heat recovery for the chiller analyzed?________ Why or why not?




What were the results of the analysis?




What vibration and noise considerations were given to the model and features of the selected chillers? 




What is the rated efficiency of each chiller at full load and the APLV, in kW/ton?






What rationale was used to select these efficiencies with the sizes?  Were more efficient models analyzed?








Attach engineering or energy simulation and economic calculations for the selections.

Are the chillers intended to be staged back and forth, depending on load, to minimize energy use? 


Will staging occur manually or automatically? 


What special control strategies will be employed with the chiller system?














What controls will be in place to allow the lowest economical entering condenser water temperature to be realized?  What other options were considered besides this strategy?






Fully describe the interface that the building automation system has with the chiller system: 










What control will the building automation system (BAS) have over the chiller system?

( BAS enables/disables the chiller, ( assigns the lead chiller, ( assigns the lead primary chilled water pump, ( assigns the lead secondary chilled water pump, ( assigns the lead condenser pump, ( assigns the lead cooling tower

The BAS monitors the following: ( LCHWT,  ( RCHWT,  ( ECDWT,  ( LCDWT, ( CDW flow, ( CHW primary flow, ( Secondary CHW flow, ( Cooling tower bypass valve,
( Chiller alarms that report to BAS (list): 






Other






The BAS can change the following: ( LCHWT setpoint, ( Reset parameters, ( ECDWT setpoint, ( Cooling tower fan staging parameters, ( Chilled water pumping pressure setpoints, ( Pressure reset parameters, ( Demand limits, ( Other






Cooling Tower

Describe the cooling tower (cross flow, counterflow, etc.) 




What are the sizes of the cooling towers?


What is the approach temperature rating of the cooling tower?




Why was a lower approach not chosen?


Attach energy and economic analyses.

Were oversized cooling towers analyzed to improve chiller efficiency?______ Why or why not?



Attach analysis.

How many motors are there per tower fan?______________  Describe.




Are the motors premium efficiency?


How is the fan speed controlled?






How do the sizes of the chillers affect the sizes of the cooling towers selected?  Are they paired? 






Can two cooling towers serve one chiller?

How are the cooling towers staged?






Will condenser water flows be monitored?_______ If not, explain why.




Will the cooling tower be used in winter?______   Why?






Air or Evaporative Cooled Condenser

( Air cooled   ( Evaporative cooled

Why was an air-cooled condenser chosen over a cooling tower?




Why was an air-cooled condenser chosen over an evaporative condenser?






Describe main features of the condensers and the chillers they serve.








Were more efficient models analyzed?  (attach analysis)








Describe the staging features







Chilled and Condenser Water Pumps 
and Piping


What pressure drop range was the piping system designed to:

( Very low pressure drop, ( Moderately low pressure drop, ( Standard pressure drop.  Was an analysis performed for using a lower pressure drop to reduce pump size and energy use?________________________________________________  Attach analysis. How were pipe losses determined?   ___rule of thumb,    ___detailed take-off and calculation,  ___other.

Are piping circuits designed to be proportionally self-balancing, to minimize the restriction (head loss) of balancing valves and circuit setters?

Describe the pumps chosen.  Primary:



Secondary:



Condenser pumps




Are they equipped with premium energy-efficient motors?


Why or why not?


How large of safety factor was considered in the pump sizing? _________________________  What was the over-sizing rationale for the pumps? ( Potential system expansion, ( Safety factor, ( Both of above.

ASHRAE 90.1 doesn’t allow flow throttling with a balancing valve more than 3 hp. Will this system comply? If no, why not? __________________________________________________
Would a more detailed head loss calculation likely result in a smaller safety factor and pump?

___________________________________________________________________________

Describe any standby or redundant pumps and their operation.






Will the control sequences allow for automatic changeover to the lag or standby pump upon pump failure and similarly for cooling tower fan failure or will manual valving be required?  Upon failure, does the lag pump or tower start or does the chiller go down and lag chiller start.  Explain fully for each:

Primary chilled water pumps:




Secondary chilled water pumps:




Condenser water pumps:




Cooling tower fans:




How is the secondary chilled water capacity controlled? ( Variable speed drives (VFD) on pumps, ( Bypass valve.  If by bypass valve, explain the rationale for not using variable speed drives and attach the economic analysis.




For VFD’s, how will the pump speed be controlled? ( Constant water pressure setpoint, ( Reset water pressure setpoint.  If the pressure is not reset, why not?




For a VFD on pressure reset, how low of speed will the pump be allowed to go?  Is this is as low as possible?  Explain.






Will chilled water flows be monitored? ( Primary flow, ( Secondary flow.   If not, explain.




Chiller System Sequence of Operations and Operating Parameters

Attach a full and comprehensive sequence of operations, including but not limited to the following conditions and systems, including all interactions:

Chiller, Cooling Tower and Pumps
· List parameter conditions that initiate start-up.

· Provide a detailed narrative of the full sequence and status and action of EACH component during EACH stage of start-up:  low load, medium load, high load, staging to next chiller, up to full load on all chillers, and then back down again to OFF condition.  List all setpoints, delays, parameters, conditions, etc., that are required to pass through each stage.  The components for which status will be given at each stage are: chiller stage and load, primary, secondary and condenser pump status, speed and flow, cooling tower stage, cooling tower bypass valve, cooling tower fans and speed, pipe pressures and setpoint resets.

Describe the sequences for the following:

· Chiller optimization staging.

· Temperature lockouts.

· Status and sequence at power outage and fire alarm.

· Effects of manual shutoff or failure of chiller, primary pump and secondary pump, condenser pump, cooling tower fan, vibration alarm.

· List all alarms.

· Include full sequences and setpoints for capacity and pressure control of the secondary chilled water system.

· Include full sequences and setpoints for condenser water temperature control and cooling tower fan control parameters.

· Cooling tower sump heater sequences, parameters and setpoints.

· List the full sequence of operation for all energy conserving strategies, including their setpoints and parameters.

· Weekend operation.

· Normal occupied and unoccupied modes.

Equipment manufacturers’ sequences and control drawings may be included, but will generally require additional narrative. Flow charts may be used if sufficiently detailed. Narrative and flow chart examples are found in Section 4 of the instructions.

For the chiller, cooling tower and pumps, the sequences are expected to be about five single-spaced, typewritten pages.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

4  Boilers and Heating Water System

4.1  Design Intent

Hot Water.  What is this heating water system used for? ( Supplies hot water to air handler units to  ___heat building space,  ___preheat incoming cold air. ( Supplies hot water to ___perimeter VAV reheat terminal units,   ___core VAV reheat terminal units.

Steam. What is the steam used for? ( Supplied to air handler units to ___heat building space,  ___preheat incoming cold air. ( Supplies hot water to ___perimeter,   ___core VAV reheat terminal units. ( Is converted to hot water in a converter before being used by the building. ( Is used for humidification of the building.
Other:


What areas of the building do the boilers serve?




List the areas that the boilers do not serve.




What types of heating equipment serve the areas not served by the boilers?




What vibration and noise considerations are given to the location of the boilers? 




What energy efficiency objectives are there for the boiler system? ( Highly efficient, ( Moderately efficient, ( Standard efficiency

What level of automatic control features are desired for this boiler system relative to automatic staging, optimization, central building automation system monitoring and control capabilities, etc.? ( Highly automated, ( Moderately automated, ( Minimally automated

What type of fuel will be used and why?   ( Natural gas,  ( Fuel oil,  ( Other




4.2 Basis of Design-Components Description and Methods for Meeting Design Intent
Boilers


The boiler is a ( Condensing,  ( Forced draft,  ( Atmospheric burner, ( Packaged,  ( Other:




Briefly describe the boiler system.

How many boilers of each size and type are there? (list number and size): 




Is there a standby / redundant boiler during design conditions?________

What method was used for determining the design heating load? 




Attach load calculations and assumptions, if not given in a previous section. (Diversity, safety factor, outdoor DB, WB, indoor DB, lighting W/sf, plug loads W/sf, sf/person, ventilation cfm/person, infiltration rate, glazing % of wall, overall U; SC).

Describe any provisions in the boiler system for accomodating future building or load expansion.







What evidence can be provided to show that the boilers are not oversized?_






Why were they chosen to be different or equal size?_






What vibration and noise considerations are given to the model and features of the chosen boilers? 




How many total stages of capacity does each boiler have?  (burner beds and stages of fire)


What is the rated efficiency of each boiler?






What rationale was used to select these efficiencies with the sizes?  Were more efficient models analyzed?








Attach engineering or energy simulation and economic calculations for the selections.

Are the boilers intended to be staged back and forth, depending on load, to minimize energy use?

Will this be done manually or automatically? 






What special control strategies will be employed with the boiler system?














Fully describe the interface that the building automation system has with the boiler system: 










What control will the building automation system (BAS) have over the boiler system?

( BAS enables/disables the boiler, ( assigns the lead boiler, ( assigns the lead primary boiler pump, ( assigns the lead secondary boiler water pump.

The BAS monitors the following: ( boiler alarm status, ( pump status, ( internal water temperature, ( steam pressure, ( HW primary flow, ( secondary HW flow, ( three-way mixing valve,  ( boiler alarms that report to BAS (list): 






Other






The BAS can change the following: ( LHWT setpoint, ( Reset parameters, ( Boiler water pumping pressure setpoints, ( Pressure reset parameters, ( Demand limits, ( Other






Will the boilers have low water cutout controls?


4.3  Heating Water Pumps and Piping

What pressure drop range was the piping system designed to?
( Very low pressure drop, ( Moderately low pressure drop, ( Standard pressure drop.  Was an analysis performed for using a lower pressure drop to reduce pump size and energy use?________________________________________________  Attach analysis. How were pipe losses determined?   ___rule of thumb,    ___detailed take-off and calculation,  ___other.

Are pipe circuits designed to be close to being self-balanced proportionally, to minimize the restriction (head loss) of balancing valves and circuit setters?

Describe the pumps chosen.  Primary:



Secondary:




Are they equipped with premium energy-efficient motors?


Why or why not?


How large of safety factor was used in the pump sizing? _________________________  What was the over-sizing rationale for the pumps? ( Potential system expansion, ( Safety factor, ( Both of above.

ASHRAE 90.1 doesn’t allow flow throttling with a balancing valve more than 3 hp. Will this system comply? If no, why not?___________________________________________________

Would a more detailed head loss calculation likely result in a smaller safety factor and pump?

___________________________________________________________________________

Describe any standby or redundant pumps and their operation.






Will the control sequences allow for automatic changeover to the lag or standby pump upon pump failure or will manual valving be required? Explain fully.

Primary heating water pumps:




Secondary heating water pumps:




How is the secondary heating water capacity controlled? ( Variable speed drives (VFD) on pumps, ( Bypass valve(s).  If bypass valves, explain the rationale for not using variable speed drives and attach the economic analysis.




For VFD’s, how will the pump speed be controlled? ( Constant water pressure setpoint, ( Reset water pressure setpoint.  If the pressure is not reset, why not?




For a VFD on pressure reset, how low of speed will the pump be allowed to go?  Is this is as low as possible?  Explain.






Will heating water flows be monitored? ( Primary flow, ( Secondary flow.   If not, explain.




How is supply water temperature controlled? ( 3-way mixing valve, ( Other




4.4  Boiler System Sequence of Operations and Operating Parameters


Attach a full and comprehensive sequence of operations, including but not limited to the following conditions and systems, including all interactions:

· List parameter conditions that initiate start-up.

· Provide a detailed narrative of the full sequence and status and action of EACH component during EACH stage of start-up:  low load, medium load, high load, staging to next boiler, up to full load on all boilers, and then back down again to OFF condition.  List all setpoints, delays, parameters, lockouts, conditions, etc., that are required to pass through each stage.  The components for which status will be given at each stage are: boiler stage and load, primary, secondary pump status, speed and flow, pipe pressures and setpoint resets.

Describe the sequences for the following:

· Boiler optimization staging.

· Temperature lockouts.

· Status and sequence at power outage and fire alarm.

· Effects of manual shutoff or failure of boiler, primary pump and secondary pump.

· List all alarms.

· Include full sequences and setpoints for capacity and pressure control of the secondary heating water system.

· List the full sequence of operation for all energy conserving strategies, including their setpoints and parameters.

· Weekend operation.

· Normal occupied and unoccupied modes.

· Warm-up mode

Equipment manufacturers’ sequences and control drawings may be included, but will generally require additional narrative. Flow charts may be used if sufficiently detailed. Narrative and flow chart examples are found in Section 4 of the instructions.

For the boiler and pumps, the sequences are expected to be about ____ single spaced, typewritten pages.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

5
Roof Top Packaged System(s) (RTU)

5.1 Design Intent


What is this system or component used for?




Systems Description


Briefly describe the system:

	( Heat pump

( Gas pack

( AC only

( Resistance coil

( Hot water

( VAV
	( Steam

( Constant volume

( Dual duct

( Multizone

( Other___________________________________________

( Other___________________________________________


List equipment and areas served:  




5.2 Basis of Design-Components Description and Methods for Meeting the Design Intent

Give size, quantity, and other specific information and the areas served, and how it will meet the objectives.

Plant

Number of units of this type: _____ 
EER (cooling): ______    Tons cooling each unit:____

Accumulated capacity for all units of this type:  Total tons cooling: ______

MBtu heating: ____________   Heat Pump COP: ______   Gas efficiency: ______

Areas served: 


Supply Fans and Capacity Control

Total CFM for packaged systems of this type:__________

( Inlet vanes   ( VFD   ( Vane axial   ( Outlet damper   ( Other: 


Motor efficiency:  ____Std. effic.,    ____Premium effic.

Return Fans / Exhaust Fans / Relief Dampers

Describe return fans, exhaust fans, or relief dampers, if any, and their function. 

Describe how building static pressure is controlled (setpoints, etc.).






VFD control:

Which fans does each VFD control?  (Supply   ( Return/Exhaust

Location of duct static-pressure sensor (distance from fan and proximity from branch takeoffs up and down stream):


Duct static pressure: ( Fixed setpoint / ( Reset or variable

Expected duct static pressure setpoint (or average if reset): _____________________

Total pressure across fan at design flow: _________[discharge pressure - suction pressure (negative)]
Minimum fan capacity (lower frequency limit setting in VFD, % of max.) ____________

Are VFD settings ( monitored or ( controlled by the BAS system? (check one)

Method used for sizing ducts _____equal friction _____static regain

Note:  Equal friction gives smaller ducts and higher pressure requirements.  If equal friction was used, was a calculation made to make sure the increased pressure and subsequent increase in energy use by the fan is more than offset by the savings in duct materials?_________If no, why not? _____________
Compressor(s)

Number of compressors per RTU: _______. Low ambient compressor package? ____

Number of condenser fans per RTU: ________.   Locked out during morning warmup? _____
Compressor capacity control; general description:

Cooling coil

Provide general description and any special features (high efficiency, face velocity, low pressure drop, etc.).  Was a low pressure drop coil analyzed?  What were the results?

Dampers

Describe the dampers and their function.











Smoke and Fire Dampers

Describe the smoke and fire damper system (location and operation).






Setpoint Temperatures

Supply air (SA): ______   SA reset (see strategy sequence): ______   Mixed air: ______

Filters

Provide general description and any special features (low pressure drop, etc.).  Were low pressure drop filters analyzed?  What were the results?________________________________

Heating System

Describe type, fuel, perimeter reheat, areas served, etc.

Economizer and OSA Dampers

( Enthalpy   ( Dry Bulb   ( Integrated   ( Economizer is first stage of cooling

Number of damper positions: (_____ or ( infinite.

Dampers closed during warm-up?   ( Yes / ( No

If dry-bulb type: OSA changeover temperature: ___________

If enthalpy:  OSA enthalpy changeover: __________________________

Other special features of the RTU:

How will the fresh air rate be maintained at low supply air volumes of the VAV system?  Are perimeter zones treated differently than interior zones (reheat box damper settings, etc.)?

How is the RTU controlled?

( Stand-alone controllers with thermostats in zones

( Above, but enabled/disabled by central building automation system (BAS)

( Integrated into BAS as below:

Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	Mixed air temp.
	______
	______
	
	Compressor stage
	
	NA

	RA temp.
	______
	NA
	
	Bldg. static pressure
	______
	______

	SA temp
	______
	______
	
	Temp. lockouts
	______
	______

	SA reset parameters
	______
	______
	
	CO2 for OSA control
	______
	______

	RA enthalpy
	______
	NA
	
	Htg. coil position
	______
	NA

	DA static pressure
	______
	______
	
	Optimum start
	NA
	______

	Duct static pressure
	______
	______
	
	Night purge
	NA
	______

	Supply fan statuc
	______
	NA
	
	Demand limit
	NA
	______

	Ret./Exh. fan status
	______
	NA
	
	Alarms (list):
	______
	______

	Supply fan speed
	______
	NA
	
	
-Dirty filter
	______
	______

	Ret./Exh. fan speed
	______
	NA
	
	
-Compressor fail
	______
	______

	Supply fan cfm
	______
	NA
	
	
-Fan loss of air
	______
	______

	Ret./Exh. fan cfm
	______
	NA
	
	
-High DA pressure
	______
	______

	Inlet vane position
	______
	NA
	
	
-Fire/smoke
	______
	______

	Filter Diff. pressure
	______
	______
	
	
-Emerg. shutdown
	______
	NA

	Occup. schedule override
	
______
	
______
	
	OSA compensation for VAV
	
______
	
______

	Night low limits
	______
	______
	
	OSA economizer
	______
	______

	_________________
	______
	______
	
	_________________
	______
	______


Describe other equipment tied to the ON/OFF status of the RTU (exhaust fans, etc.)

5.3  RTU Sequence of Operations and Operating Parameters


Provide a full and comprehensive sequence of operations, including but not limited to the following conditions and systems, including all interactions:

	Systems
	
	Conditions or Modes

	· supply fans

· exhaust fans

· return air and exhaust dampers

· supply air capacity control

· economizer and OSA dampers

· building static pressure control

· coil valve operation

· CO2 sensor OSA control

· smoke dampers
	
	· start-up

· shut-down

· normal occupied & unoccupied periods

· warm-up

· temperature lockouts

· compressor and condenser staging

· override sequences

· winter/summer changeover

· weekend operation

· normal operation heating 

· normal operation cooling 

· through deadband ranges

· alarms: fire, smoke, shutdown, equip. failure, temp. and pressure limits, etc.

· all energy conserving strategies (optimum start/stop, resets, etc.)

· fire alarm


Include the position or status at which each component resides at start-up,what occurs at fire alarm, provide all setpoints and control parameters, including all time delays.  In the sequences, describe what controls what.  That is, what components must be ON or at certain conditions in order for others to operate. Equipment manufacturers’ sequences and control drawings may be included, but will generally require additional narrative. Flow charts may be used if sufficiently detailed. Narrative and flow chart examples are found in Section 4 of the instructions.

For this RTU system, these sequences are expected to be about ______ single spaced, typewritten pages.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

6  VAV Terminal Units—Air Conditioning Only (TU_AC)

6.1  System Description


Briefly describe the TU:






Number of TU_ACs: _______   Type of area served: 


TU type:  ( pressure independent / ( pressure dependent

Minimum air damper position:  ______% open.

Are these fan powered?________.  ( Parallel,   (Series.    Why?




TU measures air flow via total and static pressure sensors.  Y/N ____.

( Cross,    ( Linear flow station?        Other flow method:


Describe TU controller type: _____________________________________________________

Damper actuator type:  ( Electric,    ( Pneumatic.  

What noise considerations were used when specifying the TU’s? _______________________

____________________________________________________________________________


Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	TU air flow
	______
	______
	
	TU air flow max.
	______
	______

	TU air flow min.
	______
	______
	
	_________________
	______
	______

	_________________
	______
	______
	
	_________________
	______
	______


6.2 TU_AC Sequence of Operations and Operating Parameters


Provide a full and comprehensive sequence of operations (including all sequences, deadband, alarm actions, etc.) on a separate sheet(s) and attach to this section of the form.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

7
VAV Terminal Units—Reheat (TU_RH)

7.1  System Description


Briefly describe the TU:




Number of TU_RHs: _______ Type of area served: 


TU type:  ( pressure independent / ( pressure dependent,   ( VAV,   ( constant volume

Are these fan powered?________.    ( Parallel,    ( Series.                                             Number of fan speeds?_______
Why?




What provisions will be made to minimize reheat?




What provisions will be made to minimize system simultaneous heating and cooling?




TU measures air flow via total and static pressure sensors.  Y/N ____.

( Cross,    ( Linear flow station?        Other flow method:


Minimum air damper position:  ______% open.

When the damper is at minimum in heating and space setpoint is not being maintained, will dampers open?________  Why?______________________________________________

Describe TU controller type: _____________________________________________________

Damper actuator type:  ( Electric,    ( Pneumatic.  

Heating coil type: ( hot water,   ( electric resistence and stages ______.

Describe heating coil valve:   ( Two position,    ( Modulating.  _______________________

Heating valve actuator type: ( Electric,    ( Pneumatic.

Do some units have 3-way valves?  Why? _________________________________________

Automatic flow control valve?___   Describe: ______________________________________

What noise considerations were used when specifying the TU’s? _______________________

____________________________________________________________________________

Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	TU air flow
	______
	______
	
	TU air flow max.
	______
	______

	TU air flow min.
	______
	______
	
	Valve position
	______
	______

	_________________
	______
	______
	
	_________________
	______
	______


7.2  TU_RH Sequence of Operations and Operating Parameters

Provide a full and comprehensive sequence of operations (including heat lockout parameters, heating valve sequences, deadbands, alarm actions, etc.) on a separate sheet(s) and attach to this section of the form.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

8
Heat Recovery Unit (HRU)

8.1  Design Intent


Describe the purpose of the HRU:




8.2  System Description


Briefly describe the system:








On which air handlers does this system operate?


Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	_________________
	______
	______
	
	_________________
	______
	______

	_________________
	______
	______
	
	_________________
	______
	______


8.3  HRU Sequence of Operations and Operating Parameters

Provide a full and comprehensive sequence of operations (including seasonal variations) on a separate sheet(s) and attach to this section of the form.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

9  Computer Room Air Conditioning Unit (CRACU)

9.1
Design Intent

What is this system or component used for?

General Description

Briefly describe the system or component.

9.2 Basis of Design-Component Description and Methods for Meeting the Design Intent


Areas served:


Number of CRACUs: _______  Sizes (tons) ____________________________  EER: 


Location of CRACU: 


( Ducted system or ( discharge only?


How is heat rejected?   ( Cooling tower / ( DX air-cooled condenser / ( Other

Location of condenser:


Humidifier description:


Reheat description:


Is there a 3-way valve in the unit? _____  Will this defeat the purpose of any variable speed drives on the chilled water system? _______________________________________________

How is the CRACU controlled?

( Stand-alone controllers with thermostats in zones

( Same, but enabled/disabled by central building automation system

( “fully” controlled by BAS

Does supply air enter this space from the main HVAC system? ( Yes / ( No

If Yes, when?




How is fresh air brought into and controlled in the space?




Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	_________________
	______
	______
	
	_________________
	______
	______

	_________________
	______
	______
	
	_________________
	______
	______


9.3  CRACU Sequence of Operations and Operating Parameters

Provide a full and comprehensive sequence of operations (including setpoints, unoccupied, occupied, fire alarm periods, etc.) on a separate sheet(s) and attach to this section of the form.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

10  Daylighting Controls

10.1  Design Intent

Briefly describe the system:









What is the primary reason for using daylighting? 
( energy savings / ( view/aesthetics


( visual light quality

What budget limitations were there? 




10.2  Basis of Design

System type:  ( continuous dimming / ( stepped dimming in ____ steps

Describe related architectural features such as light shelves, sloped ceilings, skylights, special interior finishes, intended furniture systems, etc.








How low are the lights allowed to dim? _______%.  

The system is controlled by:   ( main BAS / ( stand alone controllers

What is the light level setpoint(s) at the work plane:

	
Area
	Design Foot Candles

	_____________________________________
	    _________

	_____________________________________
	    _________

	_____________________________________
	    _________

	_____________________________________
	    _________


How deep into the building do the lights dim? _______ft.  

Are the dimming rates the same across this distance? ( Yes / ( No

Explain:




What areas of the building have dimming control?

How many zones and controllers (light sensors) are there? __________

How do occupants override the dimming?




Who has access for adjusting light levels?


Where are these adjustments made?


Where are the sensors located? 


10.3  Sequence of Operations and Operating Parameters

Provide a full and comprehensive sequence of operations (including setpoints and occupied and unoccupied conditions, etc.) on a separate sheet(s) and attach to this section of the form.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

11
Lighting Sweep Control

11.1  System Description

Briefly describe the system:






11.2  Operating Parameters

The system is controlled by:   ( Main BAS / ( Stand-alone controller

How many zones will there be? __________  Describe the zones. ______________________

____________________________________________________________________________

What is the floor area of the largest zone?


How many sweeps will there be? __________

At what times?
Weekdays: 

Saturday:

Sunday:


Describe the type of switching system that occupants will use to turn the lights back on in their zone.  




What is the maximum override duration? ________hours

Who will be able to globally override the sweeps or change the schedule?

How will the sweeps work with housekeeping schedules? 


Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

12
Building Automation System (BAS)

12.1  Design Intent 


Briefly describe the system:










Why was this system chosen over others considered?




Describe any budget limitations:




How important was energy conservation in the decision of BAS type?




12.2
Basis of Design(Component Description and Methods for 
Meeting the Design Intent



Central system is:  ( DDC, ( pneumatic

Valve actuators:  ( electric, ( pneumatic      
AHU damper actuators:  ( electric, ( pneumatic 

VAV terminal box damper actuators:  ( electric, ( pneumatic

Fire / smoke damper actuators:  ( electric, ( pneumatic

User interface:  ( graphical display of components

Limitations of the modules or features specified, compared to the highest model line system: 







Check the systems that the BAS will control (vs local equipment. packaged controllers).  Refer to the individual system section for a complete description of the points and their control by the BAS

	
	Virtually Full Control
	Partial Control
	Enable/Disable Only
	Monitor 
Only

	Rooftop packaged unit
	(
	(
	(
	(

	Air handler unit
	(
	(
	(
	(

	Terminal units
	(
	(
	(
	(

	Economizer functions
	(
	(
	(
	(

	Boiler plant
	(
	(
	(
	(

	Heating water pumping system
	(
	(
	(
	(

	Chiller plant
	(
	(
	(
	(

	Chilled water pumping system
	(
	(
	(
	(

	Cooling tower
	(
	(
	(
	(

	Condenser water pumping
	(
	(
	(
	(

	Terminal unit settings
	(
	(
	(
	(

	Heat recovery unit
	(
	(
	(
	(

	Daylighting setpoints
	(
	(
	(
	(

	Lighting sweep control
	(
	(
	(
	(

	Exterior lighting
	(
	(
	(
	(

	Computer room HVAC unit
	(
	(
	(
	(

	Fan coil unit and condenser
	(
	(
	(
	(

	Unit heaters
	(
	(
	(
	(

	Smoke and fire control
	(
	(
	(
	(

	Emergency power system
	(
	(
	(
	(

	UPS power system
	(
	(
	(
	(

	Service water heating pump
	(
	(
	(
	(

	___________________________
	(
	(
	(
	(

	___________________________
	(
	(
	(
	(

	___________________________
	(
	(
	(
	(


Location of user interface: 


Type of user interface: 

( Permanent on-site computer terminal

( Plug-in portable computer

( Remote terminal of ________________________

( Keypad only

Describe parties who will be able to change schedules only: 




Describe parties who will have full access to system: 




Check the energy conserving control strategies that will be operational in this building through the BAS.

	(
	Holiday scheduling
	(
	Occupancy-based outside air control

	(
	Zonal scheduling
	(
	DX compressor optimization

	(
	Sequential startup of equipment
	(
	Mixed air temperature control

	(
	Lighting sweep
	(
	Boiler staging and optimization

	(
	Night setup/setback
	(
	Heat element (coil) staging

	(
	Optimum start
	(
	Hot water reset

	(
	Optimum stop
	(
	Heat recovery option control

	(
	Hot & cold deck reset (supply air)
	(
	Water-side economizer control

	(
	Chilled water reset
	(
	Variable speed pump control

	(
	Chiller staging and optimization
	(
	Occupancy based HVAC control

	(
	Cooling tower component staging
	(
	Terminal regulated air volume (TRAV)

	(
	Air-side economizer control
	(
	Thermal storage control

	(
	Night ventilation purge / pre-cooling
	(
	Demand limiting or load shedding

	(
	CO2 outside air rate control
	(
	Duty cycling of equipment

	(
	VAV control-pressure independent
	(
	DHW recirculation pump control

	(
	VAV control-pressure dependent
	(
	DHW temperature control

	(
	Duct static pressure reset
	(
	Full trending capabilities

	(
	____________________________
	(
	____________________________

	(
	____________________________
	(
	____________________________

	(
	____________________________
	(
	____________________________


List all special monitoring points installed for diagnostic, performance verification and trouble shooting purposes. Which are not needed to execute the control sequences and strategies?

12.3  BAS Sequence of Operations and Operating Parameters 


Provide a full and comprehensive sequence of operations, including setpoints, deadbands, etc. List full control sequences for all control strategies. Refer to sequences already provided in other component sections, if applicable.  List on a separate sheet(s) and attach to this section of the form.

Include the position or status at which each component resides at start-up, provide all setpoints and control parameters, including all time delays.  In the sequences, describe what controls what.  That is, what components must be ON or at certain conditions in order for others to operate. Equipment manufacturers’ sequences and control drawings may be included, but will generally require additional narrative. Flow charts may be used if sufficiently detailed. Narrative and flow chart examples are found in Section 4 of the instructions.

Note:  Complete BAS description, points list with all details, program listing, etc. are not part of the design intent, but will be required as part of the O&M documentation.

12.4 Points List


For this design intent, list all points in a table that includes at least the information shown in the following example table.

	Controlled
System
	Point
Abbr.
	Point 
Description
	Display Units
	Control or Setpoint
Y/N
	Monitoring Point
Y/N
	Intermediate Point
Y/N
	Calculated Point
Y/N

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Key:
Point Description: DB temp, airflow, etc.

Control or Setpoint: Point that controls equipment and can have its setpoint changed (OSA, SAT, etc.)

Intermediate Point: Point whose value is used to make a calculation which then controls equipment (space temperatures that are averaged to a virtual point to control reset).

Monitoring Point: Point that does not control or contribute to the control of equipment, but is used for operation, maintenance, or performance verification.

Calculated Point: “Virtual” point generated from calculations of other point values.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

13
Split ___ Air Conditioning;   ___Heat Pump  System

13.1 Design Intent


What is this system or component used for?




Systems Description

Briefly describe the system:

	( DX AC only

( Heat Pump and AC

( Resistance coil

( Hot water coil

( Gas furnace
	( VAV

( Constant volume

( Dual duct

( Multizone

( Other_____________________________________________

( Other_____________________________________________


List equipment and areas served:  




13.2 Basis of Design-Component Description and Methods for Meeting the Design Intent

Give size, quantity, and other specific information and the areas served, and how it will meet the objectives.

Plant

Number of units of this type: _______ 
EER (cooling): _______  Tons cooling each: _______

Accumulated capacity for all units of this type:  Total tons cooling: ______

MBtu heating: ____________   Heat Pump COP: ______   Gas efficiency: ______

Areas served: 


Compressor(s) and Condenser(s)

Number of compressors per condenser unit: ______.  Low ambient compressor package? ____

Number of condenser fans condenser unit: ________
Compressor capacity control; general description:




Evaporator / Cooling Coil

Provide general description and any special features (high efficiency, face velocity, low pressure drop, etc.).  Was a low pressure drop coil analyzed?  What were the results?

Supply Fans and Capacity Control

Total CFM for inside fan coil or air handler of this type:_____________

( Constant volume   ( Inlet vanes   ( VFD   ( Vane axial   ( Outlet damper   ( Other: 


( Evaporator fan cycles ON and OFF with compressor.  Motor efficiency:  ____Std. effic.,   ____Premium effic.

Dampers

Describe any dampers and their function.








Smoke and Fire Dampers

Describe the smoke and fire damper system (location and operation).






Setpoint Temperatures

Supply air (SA): ______   SA reset (see strategy sequence): ______

Filters

Provide general description and any special features (low pressure drop, etc.).  Were low pressure drop filters analyzed?  What were the results?________________________________





Heating System

Describe type, fuel, perimeter reheat, areas served, etc.

Economizer and OSA Dampers

( No OSA via this unit    ( Enthalpy   ( Dry Bulb   ( Integrated   ( 
Economizer is first 
stage of cooling

Number of damper positions: (_____ or ( infinite.

Dampers closed during warm-up?   ( Yes / ( No

If dry-bulb type: OSA changeover temperature: ___________

Other special features of the split system:

How will the fresh air rate be maintained at low supply air volumes of the VAV system?  Are perimeter zones treated differently than interior zones (reheat box damper settings, etc.)?

How is the split system controlled? ________________________________________________

( Stand-alone controllers with thermostats in zones.  Number of zones: _______

( Above, but enabled/disabled by central building automation system (BAS)

( Integrated into BAS as below:

Integration of Control and Monitoring Points With the BAS
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts
	
	
Point or 
Feature
	
BAS Monitors
	BAS Can Change SetPts

	RA temp.
	______
	NA
	
	Compressor stage
	______
	NA

	SA temp
	______
	______
	
	Temp. lockouts
	______
	______

	SA reset parameters
	______
	______
	
	CO2 for OSA control
	______
	______

	RA enthalpy
	______
	NA
	
	Htg. valve position
	______
	NA

	DA static pressure
	______
	______
	
	Optimum start
	NA
	______

	Duct static pressure
	______
	______
	
	Night purge
	NA
	______

	Supply fan statuc
	______
	NA
	
	
	NA
	______

	Ret./Exh. fan status
	______
	NA
	
	Alarms (list):
	______
	______

	Occup. schedule override
	______
	______
	
	Night low limits
	______
	______

	OSA economizer
	______
	______
	
	__________________
	______
	______

	_________________
	______
	______
	
	__________________
	______
	______


Describe other equipment tied to the ON/OFF status of the split system unit (exhaust fans, etc.)



13.3  Split System Sequence of Operations and Operating Parameters


Provide a full and comprehensive sequence of operations, including but not limited to the following conditions and systems, including all interactions:

	Systems
	
	Conditions or Modes

	· supply fans

· supply air capacity control

· economizer and OSA dampers

· building static pressure control

· coil valve operation

· CO2 sensor OSA control

· smoke dampers
	
	· start-up

· shut-down

· normal occupied & unoccupied periods

· warm-up

· temperature lockouts

· compressor and condenser staging

· override sequences

· winter/summer changeover

· weekend operation

· normal operation heating 

· normal operation cooling 

· through deadband ranges

· alarms: fire, smoke, shutdown, equip. failure, temp. and pressure limits, etc.

· all energy conserving strategies (optimum start/stop, resets, etc.)

· fire alarm


Include the position or status at which each component resides at start-up,what occurs at fire alarm, provide all setpoints and control parameters, including all time delays.  In the sequences, describe what controls what.  That is, what components must be ON or at certain conditions in order for others to operate. Equipment manufacturers’ sequences and control drawings may be included, but will generally require additional narrative. Flow charts may be used if sufficiently detailed. Narrative and flow chart examples are found in Sections 4 of the instructions.

For this system, these sequences are expected to be about ______ single spaced, typewritten pages.

Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

14
Emergency Power System

14.1  Design Intent


Briefly describe the system:






What is the purpose of the emergency power and any UPS for each load other than the fire, life, safety loads?
14.2  Basis of Design-Component Description and Methods for Meeting the Design Intent
Generator

Is the generator sized to be able to handle additional loads?_________   How many?




What is the maximum time it should take the generator to be providing power from the time street power is lost (seconds)? _________________

Is there an automatic generator exercizer?


For how long should the generator be able to provide power without refueling?


Describe any special frequency and voltage regulation output requirements for the generator.




Power Quality

Describe any special power quality concerns or considerations (sensitive equipment, etc.).






UPS

How many UPS systems are there?  List all, including integral batteries in equipment.




What kind of UPS bypass will be used on the stand-alone UPS?




Emergency Power and UPS Schedule

In the following table, list each load on emergency power and/or on a UPS.  List the UPS discharge time.  List all the loads first that are only on emergency power.
	
	
	UPS

	Equipment / Loads
	On Emerg. Power (Y/N)
	On UPS (give 
UPS ID)
	Stand Alone UPS (SA) or Integral (I)
	Full Load Discharge Time (min.)

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


Applicable References


What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?

Number of sheets attached to this section: ______

15    Service Water Heating

15.1 Design Intent

Service Water. What does the system serve? ________________________________________

What energy efficient objectives are there for the service water system? __________________

____________________________________________________________________________

What is the fuel type and why?  ___Natural gas, __Electricity, __ # __ Fuel oil, __Steam, 

____ deg F water.  

___________________________________________________________________________

15.2 System Description

Service Water. Briefly describe the system. ________________________________________

15.3 Basis of Design

What is the type of water heater and why?  ___ Storage tank type, ___ Instantaneous type

What is the burner type? ___Natural draft, ___ Forced draft

Is there a return water circulation pump and why and how is it controlled? ______________

__________________________________________________________________________

If it is a non-recirculating system is there a heat trap? _______________________________

What is the water storage temperature? ___ deg F 

What is the water supply temperature? ___ deg F

Is there a mixing valve and what type? ___________________________________________

What is rated efficiency of the water heater? ______________________________________

What is the method used for determining the domestic water pipe size, storage tank size and heating load? ______________________________________________________________

Attach calculations and assumptions.

Applicable References

What are the applicable codes, guidelines, standards, regulations, criteria and other references that will be followed relating to this section?
___________________________________________________________________________

___________________________________________________________________________

Number of sheets attached to this section: ______
16
OTHER SYSTEMS NEEDING SAMPLE FORMATS
	Fire Alarm and Protection Systems
	

	
	

	Air Handler Units
	Capacity control

	
	Supply fan

	
	Return/exhaust fan and dampers

	
	Heating and cooling coil valves

	
	Economizer and OSA and return air dampers

	
	Mixed air control

	Exhaust Fans
	


USACE LEED Basis of Design Template 

(Based on PECI Model Commissioning Plan and Guide Specifications document PECI D_INTENT.V08)
1

